## Sheet1
CENTRAL PRODUCTS -Visual and Mechanical Inspection (BOB- 304-842-5996) OR 304-629-1866 OR bobedge@cp4mv.com | [14 empty] | MVSG-LLC-Visual and Mechanical Inspection(BOB- 304-942-5996)
ID | Cable Racks |  |  |  |  | Grounding | [7 empty] | Comments | ID | High Voltage Manhole is 6'x12', Cover Marked "Electric HV" | Low Voltage and Comm. Manhole is 6'x6', Cover Marked "Electric LV" or "COMM" as Required | 1" Butyl Rubber Sealant in Joints | All Excess Concrete and Grout Smooth No Rough Edges | Floor to Slope Toward Drain Points No Pockets or Non-Draining Areas | 12"x12"x4" Deep Sump Centered in Floor | Raceway Entrances |  |  | Manhole Frames & Covers |  |  |  | Embedded Pulling Iron |  | Comments
| Sufficient Numbers of Arms and Insulators | Adjustable Inserts in Concrete Walls | Insert Spacing maximum of 3' on Center Entire Inside Perimeter | Provide 6 Racks for Each Manhole, 2 Installed on Long Side & 1 On each Short Side | Arrange so Spare Raceway Ends Clear for Future Cables | 2" Hole in Floor With 1" PVC Sleeve for GND. Rod | Install 3/4"X 20" Ground Rod in Hole Provided | Attach Ground Wire to GND Rod with 3/4" Bronze Clamp | Grounding Straps Installed at Joints | Extend #4 Ground Wire Around All Four Walls | Wire Clip GND. Wire at 2' Intervals and 6" from top of Manhole | Bond Racks to Manhole GND. System | Bond Racks to Manhole GND. System | [8 empty] | Provide on all Four Sides | Provide Knockout panels or Precast Individual Raceway Openings | Proper Fit of Duct Bank Joints Proper Grout Lock | Cast Iron | Diameter - 36-1/2 Inches | Indented Solid Top Design with Two Drop Handles Each | Cover Loading - AASHTO H-20 | 3/4-Inch Diameter Stock, Fastened to Rebar Before Concrete is Placed | Located on Floor as Indicated on Sheet E5.7
A1-1 HV | [14 empty] | A1-1HV
A1-1LV | [14 empty] | A1-1LV
A1-1COM | [14 empty] | A1-1COM